## Maintenance
NAKURU MEDICROSS-20240301115028 | Patient seat repair-requires welding | 1064
HOMABAY-20240305143953 | FAULTY HAND WASHING BASIN WASHROOM | 1066
MACHAKOS-20240306124450 | kitchen sink fir repair | 1067
KIMILILI20240306 | BULB REPLACEMENT. THERE ARE LIGHTS TO BE REPLACED IN BLISS KIMILILI. FIND THE ATTACHED PHOTOS AND ELECTRICIAN'S QUOTATION | 1068
NYAMIRA-20240306155901 | FAULTY DENTAL DRAINAGE SYSTEM,URGENTLY ADDRESS THIS | 1069
NANYUKI-20240306165331 | THE BOTTOM FLUSH IS FAULTY THEREFORE THERE IS OVERFLOW OF THE WATER | 1070
KIMILILI-20240306165306 | dear team, below are the plumbing issues in bliss kimilili: laboratory hand washing sink is faulty: issue detected by plumber was burst of flexible tube kitchen sink has no tap: plumber report was that we need tap installation autoclave/housekeeping hand washing tap has leakages: plumber diagnosis indicates worn out bottle trap. attached is the plumber's requisition. plumber name: Dominic plumber contact: 0717935829. | 1071
ELDORET A-20240306180815 | PUTTING FROST STICKER ON THE PHARMACY TRANSPARENT GLASS | 1072
NYAMIRA-20240307102536 | lab had washing sink with faulty tap ,kindly facilitate its replacement,thank you | 1073
KAPSABET-20240307094004 | Repair of faulty bulbs, sockets and switch around the clinic | 1074
SUPPORT OFFICE-20240307122513 | Refrigerant gas R22a for Air Condationing units PPM/Service-Coast & Nairobi regions Facility fridges repair and service Nairobi region | 1075
SUPPORT OFFICE-20240307122513 | Hvac consumables for service and repairs in Nairobi region | 1076
KERICHO-20240307142620 | repair of 5pcs door locks and handles | 1077
NYERI 1 -20240307151934 | FACSIA LIGHTS REPAIR. FAULT DEVELOPED AFTER HEAVY DOWN POUR. FACSIA NOT VISCIBLE AT NIGHT | 1078
KERICHO-20240307151301 | bulbs in the console room and reception not working | 1079
KERUGOYA -20240307173006 | facility bulb repairs | 1080
KAKAMEGA-20240308083349 | Addition of shelves in the pharmacy | 1081
KISUMU ALIMRAN-20240308101609 | repairs of consultation/triage couches and office chairs | 1082
KISUMU ALIMRAN-20240308103743 | REPAIRS OF TAPS AND PIPES IN THE CONSULTATION 1, 3, STAFF WASHROOM, AND CM'S ROOM | 1083
WESTLANDS -20240308112821 | a/c refridgeration gas required | 1084
NYERI 1 -20240308120027 | DENTAL CHAIR UPHOLSTERY REPLACEMENT | 1085
NYERI 1 -20240308120027 | INSTALLATION OF HANDWASHING SINK AT CM OFFICE TAHT ALSO SERVES AS CONSULTATION ROOM | 1086
MURANGA-20240308125124 | all pending plumbing issues at the clinic ..the clinic will now be fully sorted with plumbing | 1087
NYERI 1 -20240308133000 | GENERATOR REPAIR AND MAINTENANCE FOR NYERI 1 | 1088
NYERI 1 -20240308133000 | NYERI 2 GENERATOR MAINTENANCE/SERVICING | 1089
MERU MEDICROSS-20240308170016 | Paint Work. Bad state of paint work in CM office and Procedure rooms. | 1090
MALINDI MEDICROSS-20240308164330 | quotation for air conditioner repairs | 1091
KISUMU ALIMRAN-20240309115816 | repair of flush handle | 1092
KISII 1-20240311115939 | bulbs replacement and electric socket repair | 1093
KISII 1-20240311115939 | REPLACEMENT OF BULBS AND REPAIR OF ELECTRICAL SWITCH ND SOCKET REPLACEMENT OF DAMAGED CELING BOARDS | 1094
NYERI 1 -20240311131739 | STORE AND KICHEN PANEL LIGHTS REPLACEMENT, SIGNAGE LIGTING TO BE INSTALLED, FLOOD LIGHTS REPLACEMENT DUE TO SECURITY REASONS, SECURITY LIGHTS OUSIDE THE THE FACILITY. THE FAULT OF THE SECURITY LIGHTS AND FLOOD LIGHTS HAPPENED AFTER A HEAVY DOWN POUR | 1095
ELDORET ZION MALL-20240311190914 | plumbing | 1096
ELDORET ZION MALL-20240311192908 | sink repair | 1097
THIKA MEDICROSS-20240312123344 | carpentry repairs | 1098
NYAMIRA-20240312150531 | loss of power suppy to the bulbs affecting the reception ,dental and lab lights,caused by shortcircuting ,rats ate some wires as seen,this also lead to destruction of two lab bulbs | 1099
KIMILILI-20240312164707 | dear team, the issues below need carpentry attention: Door leading to emergency exit has detached from the wall Door at the autoclaving room doesn't lock with ease. the frame has shifted a little bit Door at the ultrasound room doesn't lock with ease. the frame has shifted a little bit Dental door needs lock replacement Dental cabinet needs repair on one of the drawers Lab office table needs a drawer handle. attached is the carpenter's requisition. i have shared photos to Bethuel via WhatsApp since files are too large Carpenter name: Mamati Sosbin Barasa contact 0757811905 | 1100
KIMILILI-20240312171833 | BULB REPLACEMENT AT BLISS KIMILILI | 1101
KISII 1-20240313115822 | microwave repair and maintainace | 1102
KITUI -20240314125636 | roofing repair | 1103
KITUI -20240314135205 | plumbing repair for bliss kitui | 1104
KAKAMEGA-20240314161513 | Addition of shelves in the pharmacy for proper drug storage | 1105
MTWAPA-20240315141013 | entrance door welding of two broken hinges | 1106
KAKAMEGA-20240315141009 | leaking washroom sink due to faulty flaxible tube which was causing flooding of the washroom | 1107
MALINDI MEDICROSS-20240315155145 | repair of alluminium chairs | 1108
KAPSABET-20240315173819 | PROPOSED FACILITY PAINTING &FACELIFTING WORKS | 1109
KISUMU MEGACITY MEDICROSS-20240315174139 | Due to powere serge that happened today at megacity, lab/corridor AC blew up These apparatus has been providing cooling effect in lab for machines, with these crisis now majority of lab results might be affected e.g biochemistry and heamatology results. | 1110
NANYUKI-20240318115151 | THE BOTTOM FLUSH FOR LADY'S WASHROOM IS FAULTY THUS WATER IS OVERFLOWING . THE PLUMBER RECOMENDED A REPLACEMENT | 1111
NANYUKI-20240318115151 | THE WATER PUMP, PEDROLLO MACHINE IS FAULTY AND NOT REPAIRABLE. IT HAS WEAK VALVES, THE FLOWMETER HAS A LOW READING FLOW RATE THEREFORE WATER IS NOT PASSING THROUGH THE PUMP DUE TO LOW PRESSURE EVEN WHEN ITS SWITCHED ON. THERE WAS BLOCKAGE WHICH HAS BEEN REMOVED BUT THE DIAGPHRAM IS FAULTY TOO | 1112
KISII 1-20240318125642 | REPLECEMENT OF PROCEDURE ROOM BULBS | 1113
HOMABAY-20240318150143 | Generator petrol leakage | 1114
NAIVASHA-20240318162239 | Repair of leaking staff kitchen sink. bottle trap replaced. | 1115
KAPSABET-20240319100143 | REPLACEMENT/REPAIR OF FAULTY SOCKETS SERVING THE LAB BIOCHEMISTRY AND HEMATOLOGY MACHINES | 1116
KIMILILI-20240319141551 | WE Have a generator which needs installation | 1117
ELDORET ZION MALL-20240319154353 | placement of the taps to minimize contaminations | 1118
KISUMU ALIMRAN-20240319173558 | Repairs of couches for consultation 1,2,3 and triage couch and also 2 office sits | 1119
MOI AVENUE-20240319185432 | REPAIR OF BROKEN EN TOILET BOWL | 1120
MOI AVENUE-20240320104025 | REPAIR OF ROOF WHICH FELL AT THE PHYSIOTHERAPY DEPARTMENT | 1121
MALINDI MEDICROSS-20240320110701 | quotation for electric repairs malindi fn | 1122
MOI AVENUE-20240320112404 | REPAIR OF ROOF WHICH FELL AT THE PHYSIOTHERAPY DEPARTMENT | 1123
MARALAL-20240320191433 | Faulty Biomedical mechine needs repiars giving error feedback while running samples | 1125
MOI AVENUE-20240321104845 | REPAIR OF WINDOW GALSS AND PHYSIOTHERAPY EXAMINATION COUCH | 1126
MURANGA-20240321120523 | electrical gaps | 1127
HOMABAY-20240321123712 | Repaire and service of A/C at pharmacy, reception, laboratory and laboratory waiting area | 1128
KITALE -20240321140830 | Socket maintainance | 1129
WEBUYE-20240321150235 | TO FIX EACH DEFAULT BULB | 1130
NAKURU MEDICROSS-20240321152557 | change of main water line connection from the main NAWASCO line Total cost =22,340 inital approved amount=18,700 Joel approval of extra 3500 to cover the extra cost | 1131
ELDORET ZION MALL-20240321173109 | REPAIR OF CONSILTATION ROOM1 AND LABORATORY SINKS | 1132
WEBUYE-20240322102111 | BULbs need to be fixed in the clinic,9 of them will be used | 1133
KILIFI MEDICROSS-20240322115122 | plumbing works in the washroom of button top cover, rabic spray and bottle trap plus labor charges | 1136
HOMABAY-20240322165216 | Replacing faulty taps in medical facilty | 1137
MOI AVENUE-20240322181500 | REPLACEMENT OF FAULTY SOCKET IN THE PHYSIOTHERAPY DEPARTMET REBOOTING OF COOKER SOCKET IN THE AUTOCLAVING ROOM | 1138
MOI AVENUE-20240323110641 | FAULTY TOILET BOWL | 1139
NYERI 1 -20240323121245 | Generator repair/maintenance | 1143
WOTE-20240323130058 | REPAIR OF FAULTY DENTAL ROOM DRAINAGE SYSTEM LEAKING WASTE OF PROCEDURES DONE BY THE COHO. | 1145
WOTE-20240323142143 | REPLACEMENT OF FAULTY MICROWAVE MAGNETON. | 1149
KISUMU MEGA PLAZA-20240323151237 | Lighting panels blow out, 18W 3W Panellight | 1150
MERU MEDICROSS-20240325093320 | PAINT WORK FOR BADLY OFF WALLS OF THE CM OFFICE, RECEPTION PILLAR AND PROCEDURE ROOM | 1151
MERU MEDICROSS-20240325113953 | FAULTY SPIGOT, MALE PATIENTS TOILET OUT OF USE,. | 1152
MERU MEDICROSS-20240325114336 | BROKEN TAP, FORCEFUL OPENING WHEN THERE WAS WATER SHORTAGE. COMPLETELY DAMAGED, NEW PIECE NEEDED FOR REPLACEMENT. | 1153
MARALAL-20240325125820 | Overflow in Females washroom | 1154
KITALE -20240326103355 | Replacement of damaged sockes | 1155
HOMABAY-20240326114321 | Repair and service of A/C at pharmacy, reception, laboratory and laboratory waiting rea | 1156
KISII 1-20240326125459 | REPAIR OF FAULTY MICROWAVE MAGNETRON ANF PLACEMENT OF BLOWN FUSES | 1157
HOMABAY-20240326152855 | Replacement of faulty light panels at laboratory, corridor, washroom, conultation, reception ,kitchen and waiting bay area | 1158
DIANI -20240326151831 | Broken drawers | 1159
DIANI -20240326151831 | replacement of new DDA lock | 1160
SIAYA -20240326165834 | REPAIR OF FRIGERATOR | 1161
SIAYA -20240326175635 | REPAIR OF PHARMACY FRIDGE, LABORATORY FRIDGE AND KITCHEN FRIDGE | 1162
KERICHO-20240327114927 | REPAIR OFDOOR LOCKS AND HANDLES | 1163
KISUMU MEGA PLAZA-20240327120408 | General electrical repair and maintenance | 1164
KERICHO-20240327121216 | BULBING | 1165
NAKURU MEDICROSS-20240327175640 | Replacement of the siphone flusjing system | 1166
KERUGOYA -20240327181047 | UNBLOCKING LADIES WASHROOM | 1167
MACHAKOS-20240328133157 | replacement of panel lights at consultation room one and waiting bay-note that vendor selling has no ETR receipts. | 1168
HOMABAY-20240330104102 | Facility tanks cleaning and maintainance | 1169
KAKUMA -20240330124337 | GENERATOR SEVICING; LAST SERVICING WAS DONE BACK I 2021 HENCE THE MACHINE IS AT THE STATE OF BREAKING DOWN ANYTIME | 1170
KAKUMA -20240330180536 | INSTALATION OF AC UNIT IN PROCEDURE ROOM | 1171
SUPPORT OFFICE-20240402101100 | Upholstery of office chairs at CCTV/security room (4pcs) | 1172
SUPPORT OFFICE-20240402114013 | Pre-requisite tools for HVAC technician for Nyanza & Western Region | 1173
SUPPORT OFFICE-20240403120505 | Purchase of mirrors for Optical & Dental rooms and brackets for Safety Boxes | 1174
MERU MEDICROSS-20240403125850 | BLOWN TUBES IN CONSULTATION ROOM, X RAY AND ULTRASOUND ROOMS WITH INADEQUATE LIGHTING. | 1175
KISUMU MEGA PLAZA-20240403153143 | PLUMBING REPAIR AND MAINTENANCE; PRIORITY LEAKING TOILETS, BROKEN TOILET CISTERN | 1176
KABARNET-20240403163657 | Replacement of 3 blown out bulbs at the reception, triage and optical department. | 1177
KERICHO-20240404092518 | clogged and leaking toilet bowls | 1178
GITHURAI-20240404103704 | FAULTY LED BULBS | 1179
MOI AVENUE-20240404110348 | Purchase of 18 watts lights for Triage (2), Procedure room (2), waiting area (2), corridor (2),dental/theatre (2) , Ct scan room (3) | 1180
MOI AVENUE-20240404111535 | Purchase and repair of cabinet locks,2 key copies for Physiotherapy,Opg and Pharmacy store) and the pedestal locks for drawers at reception and cm office | 1181
MOI AVENUE-20240404131624 | Faulty flushing system at the gents washoom | 1182
BUSIA-20240404181858 | maintenence and servicing of the generator due to high cdonsuption of fuel | 1183
EMBU BLISS-20240405110901 | short circuit in consultaton rooms affecting the bulbs and the AC | 1184
MERU MEDICROSS-20240406083731 | tap broken beyond repair when there was water shortage. | 1185
MARALAL-20240406095432 | Installation of change over switch, purchace of cable from generator to the consumer unit | 1186
TELEPOSTA-20240406163145 | Repair and construction of carbinets in the staff changing area. | 1187
KISUMU MEGA PLAZA-20240406191944 | General plumbing repair and maintenance | 1188
MACHAKOS-20240408082452 | REPLACEMENT OF FLOURESCENT 2FT TUBE AT AUTOCLAVE ROOM | 1189
EMALI -20240408105446 | Replacement of burnt pannel lights | 1190
WESTLANDS -20240408114604 | Power extention in the dental unit, optical unit,kitchen and washroom | 1191
SUPPORT OFFICE-20240411103523 | Repair and Servicing of Air Condationing Units for Reception,Lab,Pharmacy,Dental and CMs Office- for Bliss Mtwapa | 1192
HOMABAY-20240411154934 | Replacement of Faulty generator fuel pipe | 1193
TELEPOSTA-20240411154739 | Repair of changing room and storage cabinets | 1194
MTWAPA-20240411145118 | Air conditioner maintainance and repair/replacement | 1195
KISUMU MEGA PLAZA-20240412102159 | General repair and maintenance of plumbing system. | 1196
THIKA MEDICROSS-20240412100804 | wall repairs in kitchen and triage purchase of hooks lab sample collection window | 1197
ELDORET ZION MALL-20240412133001 | ELECTRIC EXTENSION PLUG REPLACEMENT | 1198
NAKURU MEDICROSS-20240412113417 | Replacement of locks in the washroom,currently not lockable Fixing and pairing of consultation room room door to be lockable relocation of linen and equipment cabinet away from the toilet | 1199
EMALI -20240412141139 | replaceent of burnt LED lights | 1200
NAKURU MEDICROSS-20240412150124 | Making/building and installing locakge cabinets in consultation room,CM office,Radiology,Reception,Lab Addation of 1 locable cabinet for | 1201
SIAYA -20240412155601 | REPAIR/SERVICE OF GEN-SET | 1202
WESTLANDS -20240412165158 | Dental - Power Extension Optical - Display lights carpentry work- in kitchen and optical masonry | 1203
SUPPORT OFFICE-20240412180208 | Replacement of fused bulbs entrance corridor | 1204
ELDORET ZION MALL-20240413135830 | FELXPIPE AND ANCKLE VALVE FIXATION IN DENTAL ROOM | 1205
NYAMIRA-20240413160641 | faulty cuspidor bowl | 1206